## Signals
Intesis MAPS Excel signals file
PROJECT_NAME | AirSite_BACnet.ibmaps
Intesis MAPS Version | 1.2.7.0
Internal Protocol | BACnet Server
External Protocol | Modbus Master
Timestamp | 2023-07-10
# | Active | Description | Name | Type | Instance | Units | NC | Texts | # States | Rel. Def. | COV | # | Device | # Slave | Base | Read Func | Write Func | Data Length | Format | ByteOrder | Address | Bit | # Bits | Deadband | Conv. Id | Conversions
1 | False |  | Comm Error TCP Node 0 - Device 1 | 3: BI | 1 | -1 | - | - | 2 | - | - | 1 | TCP // GreenMaster // T03-3 | 60 | 1-based | - | - | - | - | - | - | - | - | - |  | -
2 | True | BT1 | Outdoor Temperature (BT1) | 0: AI | 2 | 62 | - | - | - | - | 0 | 2 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 40 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;3;-] | Enabled
3 | True | T.BT1 | Supply Air Temperature, external (T.BT1) | 0: AI | 3 | 62 | - | - | - | - | 0 | 3 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 37 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;3;-] | Enabled
4 | True | TX1 | Efficiency (TX1) | 0: AI | 4 | 98 | - | - | - | - | 0 | 4 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 21 | - | - | 0 |  | -
5 | True | T.BF1 | Supply Air Flow (T.BF1) | 0: AI | 5 | 87 | - | - | - | - | 0 | 5 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 34 | - | - | 0 |  | -
6 | True | F.BF1 | Extract Air Flow (F.BF1) | 0: AI | 6 | 87 | - | - | - | - | 0 | 6 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 36 | - | - | 0 |  | -
7 | True | H.BT1 | HC Frost Guard Temperature (H.BT1) | 0: AI | 7 | 62 | - | - | - | - | 0 | 7 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 38 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;3;-] | Enabled
8 | True | F.BT1 | Extract Air Temperature (F.BT1) | 0: AI | 8 | 62 | - | - | - | - | 0 | 8 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 39 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;3;-] | Enabled
9 | True | T.BP1 | Supply Air Duct Pressure (T.BP1) | 0: AI | 9 | 53 | - | - | - | - | 0 | 9 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 41 | - | - | 0 |  | -
10 | True | F.BP1 | Extract Air Duct Pressure (F.BP1) | 0: AI | 10 | 53 | - | - | - | - | 0 | 10 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 42 | - | - | 0 |  | -
11 | True | T.BT3 | Supply Air Temperature (T.BT3) | 0: AI | 11 | 62 | - | - | - | - | 0 | 11 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 43 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;3;-] | Enabled
12 | True | T.BT2 | Outdoor Air Temperature (T.BT2) | 0: AI | 12 | 62 | - | - | - | - | 0 | 12 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 44 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;3;-] | Enabled
13 | True | F.BT2 | Exhaust Air Temperature (F.BT2) | 0: AI | 13 | 62 | - | - | - | - | 0 | 13 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 45 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;3;-] | Enabled
14 | True | T.BP2 | Supply Air Filter Pressure (T.BP2) | 0: AI | 14 | 53 | - | - | - | - | 0 | 14 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 46 | - | - | 0 |  | -
15 | True | F.BP2 | Extract Air Filter Pressure (F.BP2) | 0: AI | 15 | 53 | - | - | - | - | 0 | 15 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 47 | - | - | 0 |  | -
16 | True | BT2 | Room Temperature (BT2) | 0: AI | 16 | 62 | - | - | - | - | 0 | 16 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 48 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;3;-] | Enabled
17 | True | Internal clock | Year | 0: AI | 17 | - | - | - | - | - | 0 | 17 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 177 | - | - | 0 |  | -
18 | True | Internal clock | Month | 0: AI | 18 | - | - | - | - | - | 0 | 18 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 178 | - | - | 0 |  | -
19 | True | Internal clock | Day | 0: AI | 19 | - | - | - | - | - | 0 | 19 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 179 | - | - | 0 |  | -
20 | True | Internal clock | Hour | 0: AI | 20 | - | - | - | - | - | 0 | 20 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 180 | - | - | 0 |  | -
21 | True | Internal clock | Minute | 0: AI | 21 | - | - | - | - | - | 0 | 21 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 181 | - | - | 0 |  | -
22 | True | Internal clock | Second | 0: AI | 22 | - | - | - | - | - | 0 | 22 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 182 | - | - | 0 |  | -
23 | True | Internal clock (1 = Monday, 7 = Sunday) | Weekday (1 = Monday, 7 = Sunday) | 0: AI | 23 | - | - | - | - | - | 0 | 23 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 183 | - | - | 0 |  | -
24 | True | T.BT1 | Temperature Regulator Current Setpoint (T.BT1) | 0: AI | 24 | 62 | - | - | - | - | 0 | 24 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 289 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;3;-] | Enabled
25 | True | T.BP1 | Supply Air Pressure Current Setpoint (T.BP1) | 0: AI | 25 | 53 | - | - | - | - | 0 | 25 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 305 | - | - | 0 |  | -
26 | True | F.BP1 | Extract Air Pressure Current Setpoint (F.BP1) | 0: AI | 26 | 53 | - | - | - | - | 0 | 26 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 321 | - | - | 0 |  | -
27 | True | T.BP1 | Setpoint Current Offset (T.BP1) | 0: AI | 27 | 53 | - | - | - | - | 0 | 27 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 701 | - | - | 0 |  | -
28 | True | F.BP1 | Setpoint Current Offset (F.BP1) | 0: AI | 28 | 53 | - | - | - | - | 0 | 28 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 702 | - | - | 0 |  | -
29 | True | T.BT1 | Setpoint Current Offset (T.BT1) | 0: AI | 29 | 54 | - | - | - | - | 0 | 29 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 0: Unsigned | 0: Big Endian | 703 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;3;-] | Enabled
30 | True | F.BP3 | Extract Air Heat Exchanger Pressure (F.BP3) | 0: AI | 30 | 53 | - | - | - | - | 0 | 30 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 817 | - | - | 0 |  | -
31 | True | Current SFP Value | SFP Value | 0: AI | 31 | 54 | - | - | - | - | 0 | 31 | TCP // GreenMaster // T03-3 | 60 | 1-based | 4: Read Input Registers | - | 16 | 3: Float | 0: Big Endian | 980 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;3;-] | Enabled
32 | True | Activation of Manual Operation for Output | SA Fan (T.GQ1) | 5: BV | 32 | - | - | - | 2 | - | - | 32 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 274 | - | - | 0 |  | -
33 | True | Activation of Manual Operation for Output | EA Fan (F.GQ1) | 5: BV | 33 | - | - | - | 2 | - | - | 33 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 275 | - | - | 0 |  | -
34 | True | Activation of Manual Operation for Output | Valve (C.QN1) | 5: BV | 34 | - | - | - | 2 | - | - | 34 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 276 | - | - | 0 |  | -
35 | True | Activation of Manual Operation for Output | Valve (H.QN1) | 5: BV | 35 | - | - | - | 2 | - | - | 35 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 277 | - | - | 0 |  | -
36 | True | Activation of Manual Operation for F.QN1 HX Bypass Damper | HX Bypass Damper (F.QN1) | 5: BV | 36 | - | - | - | 2 | - | - | 36 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 6512 | - | - | 0 |  | -
37 | True | Heating Pump Manual Override | Pump (H.GP1) | 5: BV | 37 | - | - | - | 2 | - | - | 37 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 2017 | - | - | 0 |  | -
38 | True | Cooling Pump Manual Override | Pump (C.GP1) | 5: BV | 38 | - | - | - | 2 | - | - | 38 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 2018 | - | - | 0 |  | -
39 | True | EA Damper Manual Override | Damper (F.QM1) | 5: BV | 39 | - | - | - | 2 | - | - | 39 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 2020 | - | - | 0 |  | -
40 | True | SA Damper Manual Override | Damper (T.QM1) | 5: BV | 40 | - | - | - | 2 | - | - | 40 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 2021 | - | - | 0 |  | -
41 | True | Fire Bypass Damper Manual Override | Damper (F.QM2) | 5: BV | 41 | - | - | - | 2 | - | - | 41 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 2023 | - | - | 0 |  | -
42 | True | Activation of Manual Operation for Digital Output | Activation of Manual Operation for Digital Output (H.GP1) | 5: BV | 42 | - | - | - | 2 | - | - | 42 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 2033 | - | - | 0 |  | -
43 | True | Activation of Manual Operation for Digital Output | Activation of Manual Operation for Digital Output (C.GP1) | 5: BV | 43 | - | - | - | 2 | - | - | 43 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 2034 | - | - | 0 |  | -
44 | True | Activation of Manual Operation for Digital Output | Activation of Manual Operation for Digital Output (F.QM1) | 5: BV | 44 | - | - | - | 2 | - | - | 44 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 2036 | - | - | 0 |  | -
45 | True | Activation of Manual Operation for Digital Output | Activation of Manual Operation for Digital Output (T.QM1) | 5: BV | 45 | - | - | - | 2 | - | - | 45 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 2037 | - | - | 0 |  | -
46 | True | Activation of Manual Operation for Digital Output | Activation of Manual Operation for Digital Output (F.QM2) | 5: BV | 46 | - | - | - | 2 | - | - | 46 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 2039 | - | - | 0 |  | -
47 | True | Activation of F.QN1 Winter Close Function | Winter Close Function (F.QN1) | 5: BV | 47 | - | - | - | 2 | - | - | 47 | TCP // GreenMaster // T03-3 | 60 | 1-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 12659 | - | - | 0 |  | -
48 | True | F.QN1 | Winter Close Function when BT1< this value (F.QN1 ) | 2: AV | 48 | 62 | - | - | - | - | 0 | 48 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33586 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
49 | True | Stop/Start Status (0=Running, 1=Stopped) | Stop/Start Status (0=Running, 1=Stopped) | 3: BI | 49 | - | - | - | 2 | - | - | 49 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 33 | - | - | 0 |  | -
50 | True | Digital Output | DO 1 (H.GP1 - Heating Pump Output) | 3: BI | 50 | - | - | - | 2 | - | - | 50 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 2001 | - | - | 0 |  | -
51 | True | Digital Output | DO 2 (C.GP1 - Cooling Pump Output) | 3: BI | 51 | - | - | - | 2 | - | - | 51 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 2002 | - | - | 0 |  | -
52 | True | Digital Output | DO 3 (F.GQ1 - Run Status Output) | 3: BI | 52 | - | - | - | 2 | - | - | 52 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 2003 | - | - | 0 |  | -
53 | True | Digital Output | DO 4 (F.QM1 - EA Damper Output) | 3: BI | 53 | - | - | - | 2 | - | - | 53 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 2004 | - | - | 0 |  | -
54 | True | Digital Output | DO 5 (T.QM1 - SA Damper Output) | 3: BI | 54 | - | - | - | 2 | - | - | 54 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 2005 | - | - | 0 |  | -
55 | True | Digital Output | DO 7 (F.QM2 - Fire Bypass Damper Output) | 3: BI | 55 | - | - | - | 2 | - | - | 55 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 2007 | - | - | 0 |  | -
56 | True | Digital Input Status | DI 2 (Fire) | 3: BI | 56 | - | - | - | 2 | - | - | 56 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 146 | - | - | 0 |  | -
57 | True | Digital Input Status | DI 3 (Fuse) | 3: BI | 57 | - | - | - | 2 | - | - | 57 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 147 | - | - | 0 |  | -
58 | True | Digital Input Status | DI 5 (T.GQ1 Fan Alarm) | 3: BI | 58 | - | - | - | 2 | - | - | 58 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 149 | - | - | 0 |  | -
59 | True | Digital Input Status | DI 6 (F.GQ1 Fan Alarm) | 3: BI | 59 | - | - | - | 2 | - | - | 59 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 150 | - | - | 0 |  | -
60 | True | Digital Input Status | DI 7 (F.QM2 Damper Closed) | 3: BI | 60 | - | - | - | 2 | - | - | 60 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 151 | - | - | 0 |  | -
61 | True | Digital Input Status | DI 8 (F.QM2 Damper Open) | 3: BI | 61 | - | - | - | 2 | - | - | 61 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 152 | - | - | 0 |  | -
62 | True | Digital Input Status | DI 9 (SF1 Extended Run) | 3: BI | 62 | - | - | - | 2 | - | - | 62 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 153 | - | - | 0 |  | -
63 | True | T.GQ1 (SA) | Fan is running (SA) (T.GQ1) | 3: BI | 63 | - | - | - | 2 | - | - | 63 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 241 | - | - | 0 |  | -
64 | True | F.GQ1 (EA) | Fan is running (EA) (F.GQ1) | 3: BI | 64 | - | - | - | 2 | - | - | 64 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 242 | - | - | 0 |  | -
65 | True | Alarm Status | B-Alarm (Priority B) | 3: BI | 65 | - | - | - | 2 | - | - | 65 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 287 | - | - | 0 |  | -
66 | True | Alarm Status | A-Alarm (Priority A) | 3: BI | 66 | - | - | - | 2 | - | - | 66 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 288 | - | - | 0 |  | -
67 | True | Alarm Status | Fire Alarm | 3: BI | 67 | - | - | - | 2 | - | - | 67 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 401 | - | - | 0 |  | -
68 | True | Alarm Status | Frost Guard (H.BT1) | 3: BI | 68 | - | - | - | 2 | - | - | 68 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 402 | - | - | 0 |  | -
69 | True | Alarm Status | Tripped Fuse | 3: BI | 69 | - | - | - | 2 | - | - | 69 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 404 | - | - | 0 |  | -
70 | True | Alarm Status | Temperature Regulator Deviation Alarm (T.BT1) | 3: BI | 70 | - | - | - | 2 | - | - | 70 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 405 | - | - | 0 |  | -
71 | True | Alarm Status | Regulator Deviation Alarm (SA) (T.BP1) | 3: BI | 71 | - | - | - | 2 | - | - | 71 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 406 | - | - | 0 |  | -
72 | True | Alarm Status | Regulator Deviation Alarm (F.BP1) (EA) | 3: BI | 72 | - | - | - | 2 | - | - | 72 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 407 | - | - | 0 |  | -
73 | True | Alarm Status | Fan Alarm (T.GQ1) (SA) | 3: BI | 73 | - | - | - | 2 | - | - | 73 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 408 | - | - | 0 |  | -
74 | True | Alarm Status | Fan Alarm (F.GQ1) (EA) | 3: BI | 74 | - | - | - | 2 | - | - | 74 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 409 | - | - | 0 |  | -
75 | True | Alarm Status | Low Efficiency Alarm (TX1) (HX) | 3: BI | 75 | - | - | - | 2 | - | - | 75 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 410 | - | - | 0 |  | -
76 | True | Alarm Status | High Pressure Alarm (F.BP3) | 3: BI | 76 | - | - | - | 2 | - | - | 76 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 411 | - | - | 0 |  | -
77 | True | Alarm Status | Filter Alarm (T.BP2) (SA) | 3: BI | 77 | - | - | - | 2 | - | - | 77 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 412 | - | - | 0 |  | -
78 | True | Alarm Status | Filter Alarm (F.BP2) (EA) | 3: BI | 78 | - | - | - | 2 | - | - | 78 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 413 | - | - | 0 |  | -
79 | True | Alarm Status | Smoke Detector Service Alarm | 3: BI | 79 | - | - | - | 2 | - | - | 79 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 414 | - | - | 0 |  | -
80 | True | Alarm Status | Sum Alarm for all QM (Dampers) | 3: BI | 80 | - | - | - | 2 | - | - | 80 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 415 | - | - | 0 |  | -
81 | True | Digital Output | SC2.1.DO1 - T.QM1.1 | 3: BI | 81 | - | - | - | 2 | - | - | 81 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 5905 | - | - | 0 |  | -
82 | True | Digital Output | SC2.1.DO2 - T.QM1.2 | 3: BI | 82 | - | - | - | 2 | - | - | 82 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 5921 | - | - | 0 |  | -
83 | True | Digital Output | SC2.2.DO1 - T.QM1.3 | 3: BI | 83 | - | - | - | 2 | - | - | 83 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 5937 | - | - | 0 |  | -
84 | True | Digital Output | SC2.2.DO2 - T.QM1.4 | 3: BI | 84 | - | - | - | 2 | - | - | 84 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 5953 | - | - | 0 |  | -
85 | True | Digital Output | SC2.3.DO1 - T.QM1.5 | 3: BI | 85 | - | - | - | 2 | - | - | 85 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 5969 | - | - | 0 |  | -
86 | True | Digital Output | SC2.3.DO2 - T.QM1.6 | 3: BI | 86 | - | - | - | 2 | - | - | 86 | TCP // GreenMaster // T03-3 | 60 | 1-based | 2: Read Discrete Inputs | - | 1 | - | - | 5985 | - | - | 0 |  | -
87 | True | Alarm Reset | Alarm Reset | 2: AV | 87 | - | - | - | - | - | 0 | 87 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 32 | - | - | 0 |  | -
88 | True | T.GQ1 | SA Fan Output Value (T.GQ1 ) | 2: AV | 88 | - | - | - | - | - | 0 | 88 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 50 | - | - | 0 | DIRECTION[</>]:INDEXES[-;10;-;-] | Enabled
89 | True | F.GQ1 | EA Fan Output Value (F.GQ1) | 2: AV | 89 | - | - | - | - | - | 0 | 89 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 51 | - | - | 0 | DIRECTION[</>]:INDEXES[-;10;-;-] | Enabled
90 | True | C.QN1 | Cooling Control Valve Output Value (C.QN1) | 2: AV | 90 | - | - | - | - | - | 0 | 90 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 52 | - | - | 0 | DIRECTION[</>]:INDEXES[-;10;-;-] | Enabled
91 | True | H.QN1 | Heating Control Valve Output Value (H.QN1) | 2: AV | 91 | - | - | - | - | - | 0 | 91 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 53 | - | - | 0 | DIRECTION[</>]:INDEXES[-;10;-;-] | Enabled
92 | True | F.QN1 | HX Bypass Damper Output Value (F.QN1) | 2: AV | 92 | - | - | - | - | - | 0 | 92 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 369 | - | - | 0 | DIRECTION[</>]:INDEXES[-;10;-;-] | Enabled
93 | True | Unit Start/Stop | Unit Start/Stop | 2: AV | 93 | - | - | - | - | - | 0 | 93 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 32772 | - | - | 0 |  | -
94 | True | T.BT1 | Temperature Regulator - P-Band (T.BT1) | 2: AV | 94 | 62 | - | - | - | - | 0 | 94 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33059 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
95 | True | T.BT1 | Temperature Regulator - I-time (T.BT1) | 2: AV | 95 | 73 | - | - | - | - | 0 | 95 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33061 | - | - | 0 |  | -
96 | True | T.GQ1 | Max Limitation Value T.GQ1 (T.GQ1) | 2: AV | 96 | - | - | - | - | - | 0 | 96 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33083 | - | - | 0 | DIRECTION[</>]:INDEXES[-;10;-;-] | Enabled
97 | True | F.GQ1 | Max Limitation Value F.GQ1 (F.GQ1) | 2: AV | 97 | - | - | - | - | - | 0 | 97 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33099 | - | - | 0 | DIRECTION[</>]:INDEXES[-;10;-;-] | Enabled
98 | True | H.BT1 | Frost Guard Regulator - Setpoint (H.BT1) | 2: AV | 98 | 62 | - | - | - | - | 0 | 98 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33121 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
99 | True | H.BT1 | Frost Guard Regulator - P-Band (H.BT1) | 2: AV | 99 | 62 | - | - | - | - | 0 | 99 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33123 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
100 | True | H.BT1 | Frost Guard Regulator - I-time (H.BT1) | 2: AV | 100 | 62 | - | - | - | - | 0 | 100 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33125 | - | - | 0 |  | -
101 | True | T.BT1 | Temperature Regulator - Alarm Delay (T.BT1) | 2: AV | 101 | 73 | - | - | - | - | 0 | 101 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33285 | - | - | 0 |  | -
102 | True | T.BP1 | (SA) Duct Pressure Regulator - Alarm Delay (T.BP1) | 2: AV | 102 | 73 | - | - | - | - | 0 | 102 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33286 | - | - | 0 |  | -
103 | True | F.BP1 | (EA) Duct Pressure Regulator - Alarm Delay (F.BP1) | 2: AV | 103 | 73 | - | - | - | - | 0 | 103 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33287 | - | - | 0 |  | -
104 | True | T.GQ1 | (SA) - Fan Alarm Delay (T.GQ1) | 2: AV | 104 | 73 | - | - | - | - | 0 | 104 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33288 | - | - | 0 |  | -
105 | True | F.GQ1 | (EA) - Fan Alarm Delay (F.GQ1) | 2: AV | 105 | 73 | - | - | - | - | 0 | 105 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33289 | - | - | 0 |  | -
106 | True | TX1 | (HX) - Low Efficiency Alarm Delay (TX1) | 2: AV | 106 | 73 | - | - | - | - | 0 | 106 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33290 | - | - | 0 |  | -
107 | True | F.BP3 | Defrost Alarm Delay (F.BP3) | 2: AV | 107 | 73 | - | - | - | - | 0 | 107 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33291 | - | - | 0 |  | -
108 | True | T.BP2 | (SA) Filter Alarm Delay (T.BP2) | 2: AV | 108 | 73 | - | - | - | - | 0 | 108 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33292 | - | - | 0 |  | -
109 | True | F.BP2 | (EA) Filter Alarm Delay (F.BP2) | 2: AV | 109 | 73 | - | - | - | - | 0 | 109 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33293 | - | - | 0 |  | -
110 | True | Smoke | Smoke Detector Service Alarm Delay | 2: AV | 110 | 73 | - | - | - | - | 0 | 110 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33294 | - | - | 0 |  | -
111 | True | T.BT1 | Temperature Regulator - Setpoint (Setting) (T.BT1) | 2: AV | 111 | 62 | - | - | - | - | 0 | 111 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33329 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
112 | True | H.GP1 | Low Temperature Start Temp (H.GP1) | 2: AV | 112 | 62 | - | - | - | - | 0 | 112 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33330 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
113 | True | H.GP1 | Low Temperature Hysteresis (H.GP1) | 2: AV | 113 | 62 | - | - | - | - | 0 | 113 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33331 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
114 | True | H.BT1 | Frost Guard Unit Stop Temperature (H.BT1) | 2: AV | 114 | 62 | - | - | - | - | 0 | 114 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33332 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
115 | True | H.BT1 | Frost Guard Unit Stop Hysteresis (H.BT1) | 2: AV | 115 | 62 | - | - | - | - | 0 | 115 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33333 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
116 | True | F.BT1 | Fire Alarm Temperature (F.BT1) | 2: AV | 116 | 62 | - | - | - | - | 0 | 116 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33334 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
117 | True | TX1 | (HX) Low Efficiency Alt. 1 Alarm Level (TX1) | 2: AV | 117 | 98 | - | - | - | - | 0 | 117 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33335 | - | - | 0 |  | -
118 | True | T.BT1 | Temperature Regulator - Deviation Alarm Level (T.BT1) | 2: AV | 118 | 62 | - | - | - | - | 0 | 118 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33337 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
119 | True | T.GQ1 | Value During Fire T.GQ1 (T.GQ1) | 2: AV | 119 | - | - | - | - | - | 0 | 119 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33338 | - | - | 0 | DIRECTION[</>]:INDEXES[-;10;-;-] | Enabled
120 | True | T.BT1 | Temperature Regulator - Min. Value (T.BT1) | 2: AV | 120 | 62 | - | - | - | - | 0 | 120 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33341 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
121 | True | T.BT1 | Temperature Regulator - Max. Value (T.BT1) | 2: AV | 121 | 62 | - | - | - | - | 0 | 121 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33342 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
122 | True | T.GQ1 | (SA) - Fan Startup Delay (T.GQ1) | 2: AV | 122 | 73 | - | - | - | - | 0 | 122 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33343 | - | - | 0 |  | -
123 | True | F.GQ1 | (EA) - Fan Startup Delay (F.GQ1) | 2: AV | 123 | 73 | - | - | - | - | 0 | 123 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33344 | - | - | 0 |  | -
124 | True | F.GQ1 | Value During Fire F.GQ1 (F.GQ1) | 2: AV | 124 | - | - | - | - | - | 0 | 124 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33354 | - | - | 0 | DIRECTION[</>]:INDEXES[-;10;-;-] | Enabled
125 | True | H.GP1/C.GP1 | Exercise Interval H.GP1/C.GP1 (H.GP1/C.GP1) | 2: AV | 125 | 72 | - | - | - | - | 0 | 125 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33363 | - | - | 0 |  | -
126 | True | H.GP1/C.GP1 | Exercise Time H.GP1/C.GP1 (H.GP1/C.GP1) | 2: AV | 126 | 73 | - | - | - | - | 0 | 126 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33364 | - | - | 0 |  | -
127 | True | F.QM2 | Exercise Interval F.QM2 (F.QM2) | 2: AV | 127 | 72 | - | - | - | - | 0 | 127 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33365 | - | - | 0 |  | -
128 | True | F.QM2 | Exercise Time F.QM2 (F.QM2) | 2: AV | 128 | 73 | - | - | - | - | 0 | 128 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33366 | - | - | 0 |  | -
129 | True | T.BP1 | (SA) Pressure Regulator - Setpoint (Setting) (T.BP1) | 2: AV | 129 | 53 | - | - | - | - | 0 | 129 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33377 | - | - | 0 |  | -
130 | True | T.BP1 | (SA) Pressure Regulator - P-Band (T.BP1) | 2: AV | 130 | 53 | - | - | - | - | 0 | 130 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33379 | - | - | 0 |  | -
131 | True | T.BP1 | (SA) Pressure Regulator - I-time (T.BP1) | 2: AV | 131 | 73 | - | - | - | - | 0 | 131 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33381 | - | - | 0 |  | -
132 | True | T.BP1 | (SA) Pressure Regulator - Deviation Alarm Level (T.BP1) | 2: AV | 132 | 53 | - | - | - | - | 0 | 132 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33383 | - | - | 0 |  | -
133 | True | F.BP1 | (EA) Pressure Regulator - Setpoint (Setting) (F.BP1) | 2: AV | 133 | 53 | - | - | - | - | 0 | 133 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33384 | - | - | 0 |  | -
134 | True | F.BP1 | (EA) Pressure Regulator - P-Band (F.BP1) | 2: AV | 134 | 53 | - | - | - | - | 0 | 134 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33386 | - | - | 0 |  | -
135 | True | F.BP1 | (EA) Pressure Regulator - I-time (F.BP1) | 2: AV | 135 | 73 | - | - | - | - | 0 | 135 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33388 | - | - | 0 |  | -
136 | True | F.BP1 | (EA) Pressure Regulator - Deviation Alarm Level (F.BP1) | 2: AV | 136 | 53 | - | - | - | - | 0 | 136 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33390 | - | - | 0 |  | -
137 | True | T.BP2 | Supply Air Filter - Alarm Level Dirty Filter (T.BP2) | 2: AV | 137 | 53 | - | - | - | - | 0 | 137 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33391 | - | - | 0 |  | -
138 | True | F.BP2 | Extract Air Filter - Alarm Level Dirty Filter (F.BP2) | 2: AV | 138 | 53 | - | - | - | - | 0 | 138 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33392 | - | - | 0 |  | -
139 | True | Time Channel | Monday - Start Hour | 2: AV | 139 | 71 | - | - | - | - | 0 | 139 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33393 | - | - | 0 |  | -
140 | True | Time Channel | Monday - Stop Hour | 2: AV | 140 | 71 | - | - | - | - | 0 | 140 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33394 | - | - | 0 |  | -
141 | True | Time Channel | Tuesday - Start Hour | 2: AV | 141 | 71 | - | - | - | - | 0 | 141 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33395 | - | - | 0 |  | -
142 | True | Time Channel | Tuesday - Stop Hour | 2: AV | 142 | 71 | - | - | - | - | 0 | 142 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33396 | - | - | 0 |  | -
143 | True | Time Channel | Wednesday - Start Hour | 2: AV | 143 | 71 | - | - | - | - | 0 | 143 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33397 | - | - | 0 |  | -
144 | True | Time Channel | Wednesday - Stop Hour | 2: AV | 144 | 71 | - | - | - | - | 0 | 144 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33398 | - | - | 0 |  | -
145 | True | Time Channel | Thursday - Start Hour | 2: AV | 145 | 71 | - | - | - | - | 0 | 145 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33399 | - | - | 0 |  | -
146 | True | Time Channel | Thursday - Stop Hour | 2: AV | 146 | 71 | - | - | - | - | 0 | 146 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33400 | - | - | 0 |  | -
147 | True | Time Channel | Friday - Start Hour | 2: AV | 147 | 71 | - | - | - | - | 0 | 147 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33401 | - | - | 0 |  | -
148 | True | Time Channel | Friday - Stop Hour | 2: AV | 148 | 71 | - | - | - | - | 0 | 148 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33402 | - | - | 0 |  | -
149 | True | Time Channel | Saturday - Start Hour | 2: AV | 149 | 71 | - | - | - | - | 0 | 149 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33403 | - | - | 0 |  | -
150 | True | Time Channel | Saturday - Stop Hour | 2: AV | 150 | 71 | - | - | - | - | 0 | 150 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33404 | - | - | 0 |  | -
151 | True | Time Channel | Sunday - Start Hour | 2: AV | 151 | 71 | - | - | - | - | 0 | 151 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33405 | - | - | 0 |  | -
152 | True | Time Channel | Monday - Start Minute | 2: AV | 152 | 72 | - | - | - | - | 0 | 152 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33505 | - | - | 0 |  | -
153 | True | Time Channel | Monday - Stop Minute | 2: AV | 153 | 72 | - | - | - | - | 0 | 153 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33506 | - | - | 0 |  | -
154 | True | Time Channel | Tuesday - Start Minute | 2: AV | 154 | 72 | - | - | - | - | 0 | 154 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33507 | - | - | 0 |  | -
155 | True | Time Channel | Tuesday - Stop Minute | 2: AV | 155 | 72 | - | - | - | - | 0 | 155 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33508 | - | - | 0 |  | -
156 | True | Time Channel | Wednesday - Start Minute | 2: AV | 156 | 72 | - | - | - | - | 0 | 156 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33509 | - | - | 0 |  | -
157 | True | Time Channel | Wednesday - Stop Minute | 2: AV | 157 | 72 | - | - | - | - | 0 | 157 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33510 | - | - | 0 |  | -
158 | True | Time Channel | Thursday - Start Minute | 2: AV | 158 | 72 | - | - | - | - | 0 | 158 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33511 | - | - | 0 |  | -
159 | True | Time Channel | Thursday - Stop Minute | 2: AV | 159 | 72 | - | - | - | - | 0 | 159 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33512 | - | - | 0 |  | -
160 | True | Time Channel | Friday - Start Minute | 2: AV | 160 | 72 | - | - | - | - | 0 | 160 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33513 | - | - | 0 |  | -
161 | True | Time Channel | Friday - Stop Minute | 2: AV | 161 | 72 | - | - | - | - | 0 | 161 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33514 | - | - | 0 |  | -
162 | True | Time Channel | Saturday - Start Minute | 2: AV | 162 | 72 | - | - | - | - | 0 | 162 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33515 | - | - | 0 |  | -
163 | True | Time Channel | Saturday - Stop Minute | 2: AV | 163 | 72 | - | - | - | - | 0 | 163 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33516 | - | - | 0 |  | -
164 | True | Time Channel | Sunday - Start Minute | 2: AV | 164 | 72 | - | - | - | - | 0 | 164 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33517 | - | - | 0 |  | -
165 | True | Time Channel | Sunday - Stop Minute | 2: AV | 165 | 72 | - | - | - | - | 0 | 165 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33518 | - | - | 0 |  | -
166 | True | Time Channel | Sunday - Stop Hour | 2: AV | 166 | 71 | - | - | - | - | 0 | 166 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33406 | - | - | 0 |  | -
167 | True | Temp. Regulator | Setpoint Curve - Offset Temp 1 | 2: AV | 167 | 62 | - | - | - | - | 0 | 167 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33409 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
168 | True | Temp. Regulator | Setpoint Curve - Offset Temp 2 | 2: AV | 168 | 62 | - | - | - | - | 0 | 168 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33410 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
169 | True | Temp. Regulator | Setpoint Curve - Offset Temp 3 | 2: AV | 169 | 62 | - | - | - | - | 0 | 169 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33411 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
170 | True | Temp. Regulator | Setpoint Curve - Offset Temp 4 | 2: AV | 170 | 62 | - | - | - | - | 0 | 170 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33412 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
171 | True | Temp. Regulator | Setpoint Curve - Offset Temp 5 | 2: AV | 171 | 62 | - | - | - | - | 0 | 171 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33413 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
172 | True | Temp. Regulator | Setpoint Curve - Offset Temp 6 | 2: AV | 172 | 62 | - | - | - | - | 0 | 172 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33414 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
173 | True | Temp. Regulator | Setpoint Curve - Offset Temp 7 | 2: AV | 173 | 62 | - | - | - | - | 0 | 173 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33415 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
174 | True | Temp. Regulator | Setpoint Curve - Offset Temp 8 | 2: AV | 174 | 62 | - | - | - | - | 0 | 174 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33416 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
175 | True | Temp. Regulator | Setpoint Curve - Offset Temp 9 | 2: AV | 175 | 62 | - | - | - | - | 0 | 175 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33417 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
176 | True | Temp. Regulator | Setpoint Curve - Temp 1 | 2: AV | 176 | 62 | - | - | - | - | 0 | 176 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33425 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
177 | True | Temp. Regulator | Setpoint Curve - Temp 2 | 2: AV | 177 | 62 | - | - | - | - | 0 | 177 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33426 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
178 | True | Temp. Regulator | Setpoint Curve - Temp 3 | 2: AV | 178 | 62 | - | - | - | - | 0 | 178 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33427 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
179 | True | Temp. Regulator | Setpoint Curve - Temp 4 | 2: AV | 179 | 62 | - | - | - | - | 0 | 179 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33428 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
180 | True | Temp. Regulator | Setpoint Curve - Temp 5 | 2: AV | 180 | 62 | - | - | - | - | 0 | 180 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33429 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
181 | True | Temp. Regulator | Setpoint Curve - Temp 6 | 2: AV | 181 | 62 | - | - | - | - | 0 | 181 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33430 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
182 | True | Temp. Regulator | Setpoint Curve - Temp 7 | 2: AV | 182 | 62 | - | - | - | - | 0 | 182 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33431 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
183 | True | Temp. Regulator | Setpoint Curve - Temp 8 | 2: AV | 183 | 62 | - | - | - | - | 0 | 183 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33432 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
184 | True | Temp. Regulator | Setpoint Curve - Temp 9 | 2: AV | 184 | 62 | - | - | - | - | 0 | 184 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33433 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
185 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Pressure 1 | 2: AV | 185 | 53 | - | - | - | - | 0 | 185 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33441 | - | - | 0 |  | -
186 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Pressure 2 | 2: AV | 186 | 53 | - | - | - | - | 0 | 186 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33442 | - | - | 0 |  | -
187 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Pressure 3 | 2: AV | 187 | 53 | - | - | - | - | 0 | 187 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33443 | - | - | 0 |  | -
188 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Pressure 4 | 2: AV | 188 | 53 | - | - | - | - | 0 | 188 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33444 | - | - | 0 |  | -
189 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Pressure 5 | 2: AV | 189 | 53 | - | - | - | - | 0 | 189 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33445 | - | - | 0 |  | -
190 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Pressure 6 | 2: AV | 190 | 53 | - | - | - | - | 0 | 190 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33446 | - | - | 0 |  | -
191 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Pressure 7 | 2: AV | 191 | 53 | - | - | - | - | 0 | 191 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33447 | - | - | 0 |  | -
192 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Pressure 8 | 2: AV | 192 | 53 | - | - | - | - | 0 | 192 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33448 | - | - | 0 |  | -
193 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Pressure 9 | 2: AV | 193 | 53 | - | - | - | - | 0 | 193 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33449 | - | - | 0 |  | -
194 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Temp 1 | 2: AV | 194 | 62 | - | - | - | - | 0 | 194 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33457 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
195 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Temp 2 | 2: AV | 195 | 62 | - | - | - | - | 0 | 195 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33458 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
196 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Temp 3 | 2: AV | 196 | 62 | - | - | - | - | 0 | 196 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33459 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
197 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Temp 4 | 2: AV | 197 | 62 | - | - | - | - | 0 | 197 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33460 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
198 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Temp 5 | 2: AV | 198 | 62 | - | - | - | - | 0 | 198 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33461 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
199 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Temp 6 | 2: AV | 199 | 62 | - | - | - | - | 0 | 199 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33462 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
200 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Temp 7 | 2: AV | 200 | 62 | - | - | - | - | 0 | 200 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33463 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
201 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Temp 8 | 2: AV | 201 | 62 | - | - | - | - | 0 | 201 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33464 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
202 | True | T.BP1 (SA) | Setpoint Offset Curve - (T.BP1) (SA) Temp 9 | 2: AV | 202 | 62 | - | - | - | - | 0 | 202 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33465 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
203 | True | F.BP1 (SA) | Setpoint Offset Curve - (F.BP1) (SA) Pressure 1 | 2: AV | 203 | 53 | - | - | - | - | 0 | 203 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33473 | - | - | 0 |  | -
204 | True | F.BP1 (SA) | Setpoint Offset Curve - (F.BP1) (SA) Pressure 2 | 2: AV | 204 | 53 | - | - | - | - | 0 | 204 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33474 | - | - | 0 |  | -
205 | True | F.BP1 (SA) | Setpoint Offset Curve - (F.BP1) (SA) Pressure 3 | 2: AV | 205 | 53 | - | - | - | - | 0 | 205 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33475 | - | - | 0 |  | -
206 | True | F.BP1 (SA) | Setpoint Offset Curve - (F.BP1) (SA) Pressure 4 | 2: AV | 206 | 53 | - | - | - | - | 0 | 206 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33476 | - | - | 0 |  | -
207 | True | F.BP1 (SA) | Setpoint Offset Curve - (F.BP1) (SA) Pressure 5 | 2: AV | 207 | 53 | - | - | - | - | 0 | 207 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33477 | - | - | 0 |  | -
208 | True | F.BP1 (SA) | Setpoint Offset Curve - (F.BP1) (SA) Pressure 6 | 2: AV | 208 | 53 | - | - | - | - | 0 | 208 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33478 | - | - | 0 |  | -
209 | True | F.BP1 (SA) | Setpoint Offset Curve - (F.BP1) (SA) Pressure 7 | 2: AV | 209 | 53 | - | - | - | - | 0 | 209 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33479 | - | - | 0 |  | -
210 | True | F.BP1 (SA) | Setpoint Offset Curve - (F.BP1) (SA) Pressure 8 | 2: AV | 210 | 53 | - | - | - | - | 0 | 210 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33480 | - | - | 0 |  | -
211 | True | F.BP1 (SA) | Setpoint Offset Curve - (F.BP1) (SA) Pressure 9 | 2: AV | 211 | 53 | - | - | - | - | 0 | 211 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33481 | - | - | 0 |  | -
212 | True | F.BP1 (EA) | Setpoint Offset Curve - (F.BP1) (EA) Temp 1 | 2: AV | 212 | 62 | - | - | - | - | 0 | 212 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33489 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
213 | True | F.BP1 (EA) | Setpoint Offset Curve - (F.BP1) (EA) Temp 2 | 2: AV | 213 | 62 | - | - | - | - | 0 | 213 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33490 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
214 | True | F.BP1 (EA) | Setpoint Offset Curve - (F.BP1) (EA) Temp 3 | 2: AV | 214 | 62 | - | - | - | - | 0 | 214 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33491 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
215 | True | F.BP1 (EA) | Setpoint Offset Curve - (F.BP1) (EA) Temp 4 | 2: AV | 215 | 62 | - | - | - | - | 0 | 215 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33492 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
216 | True | F.BP1 (EA) | Setpoint Offset Curve - (F.BP1) (EA) Temp 5 | 2: AV | 216 | 62 | - | - | - | - | 0 | 216 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33493 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
217 | True | F.BP1 (EA) | Setpoint Offset Curve - (F.BP1) (EA) Temp 6 | 2: AV | 217 | 62 | - | - | - | - | 0 | 217 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33494 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
218 | True | F.BP1 (EA) | Setpoint Offset Curve - (F.BP1) (EA) Temp 7 | 2: AV | 218 | 62 | - | - | - | - | 0 | 218 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33495 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
219 | True | F.BP1 (EA) | Setpoint Offset Curve - (F.BP1) (EA) Temp 8 | 2: AV | 219 | 62 | - | - | - | - | 0 | 219 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33496 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
220 | True | F.BP1 (EA) | Setpoint Offset Curve - (F.BP1) (EA) Temp 9 | 2: AV | 220 | 62 | - | - | - | - | 0 | 220 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 1: Signed (C2) | 0: Big Endian | 33497 | - | - | 0 | DIRECTION[</>]:INDEXES[-;3;-;-] | Enabled
221 | True | F.BP3 (HX High Pressure) | Deviation Alarm Level (F.BP3) (HX High Pressure) | 2: AV | 221 | 53 | - | - | - | - | 0 | 221 | TCP // GreenMaster // T03-3 | 60 | 1-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 33541 | - | - | 0 |  | -

## BACnet Server
Units
-
ampere_square_meters (169)
amperes (3)
amperes_per_meter (167)
amperes_per_square_meter (168)
bars (55)
becquerels (222)
btus (20)
btus_per_hour (50)
btus_per_pound (117)
btus_per_pound_dry_air (24)
centimeters(118)
meters (31)
centimeters_of_mercury (60)
centimeters_of_water (57)
cubic_feet (79)
cubic_feet_per_hour (191)
cubic_feet_per_minute (84)
cubic_feet_per_second (142)
cubic_meters (80)
cubic_meters_per_hour (135)
cubic_meters_per_minute (165)
cubic_meters_per_second (85)
currency1 (105)
currency10 (114)
currency2 (106)
currency3 (107)
currency4 (108)
currency5 (109)
currency6 (110)
currency7 (111)
currency8 (112)
currency9 (113)
cycles_per_hour (25)
cycles_per_minute (26)
days (70)
decibels (199)
decibels_a (232)
decibels_millivolt (200)
decibels_volt (201)
degree_days_Celsius (65)
degree_days_Fahrenheit (66)
degrees_angular (90)
degrees_Celsius (62)
degrees_Celsius_per_hour (91)
degrees_Celsius_per_minute (92)
degrees_Fahrenheit (64)
degrees_Fahrenheit_per_hour (93)
degrees_Fahrenheit_per_minute (94)
degrees_Kelvin (63)
degrees_Kelvin_per_hour (181)
degrees_Kelvin_per_minute (182)
degrees_phase (14)
delta_degrees_Fahrenheit (120)
delta_degrees_Kelvin (121)
farads (170)
feet(33)
candelas_per_square_meter (180)
feet_per_minute (77)
feet_per_second (76)
grams_of_water_per_kilogram_dry_air(28)
micrometers (194)
grams_per_cubic_centimeter (221)
grams_per_cubic_meter (217)
grams_per_gram (208)
grams_per_kilogram (210)
grams_per_liter (214)
grams_per_milliliter (213)
grams_per_square_meter (235)
gray (225)
hectopascals (133)
henrys (171)
hertz (27)
horsepower (51)
hours (71)
hundredths_seconds (158)
imperial_gallons (81)
imperial_gallons_per_minute (86)
inches_of_mercury (61)
inches_of_water (58)
joule_seconds (183)
joules (16)
joules_per_degree_Kelvin (127)
joules_per_kilogram_degree_Kelvin (128)
joules_per_kilogram_dry_air (23)
kilo_btus (147)
kilo_btus_per_hour (157)
kilobecquerels (223)
kilograms_per_cubic_meter (186)
kilograms_per_hour (44)
kilograms_per_kilogram (209)
kilograms_per_minute (43)
kilograms_per_second (42)
kilohertz (129)
kilohms (122)
kilojoules (17)
kilojoules_per_degree_Kelvin (151)
kilojoules_per_kilogram (125)
kilojoules_per_kilogram_dry_air (149)
kilometers_per_hour (75)
kilopascals (54)
kilovolt_amperes (9)
kilovolt_amperes_reactive (12)
kilovolts (6)
kilowatt_hours (19)
kilowatt_hours_per_square_foot (138)
kilowatt_hours_per_square_meter (137)
kilowatt_hours_reactive (204)
kilowatts (48)
liters (82)
liters_per_hour (136)
liters_per_minute (88)
liters_per_second (87)
mega_btus (148)
megabecquerels (224)
megahertz (130)
megajoules (126)
megajoules_per_degree_Kelvin (152)
megajoules_per_kilogram_dry_air (150)
megajoules_per_square_foot (140)
megajoules_per_square_meter (139)
megavolt_amperes (10)
megavolt_amperes_reactive (13)
megavolts (7)
megawatt_hours (146)
megawatt_hours_reactive (205)
megawatts (49)
megohms (123)
meters_per_hour (164)
meters_per_minute (163)
meters_per_second (74)
micrograms_per_cubic_meter (219)
micrograms_per_liter (216)
microgray (227)
microsiemens (190)
microsieverts (230)
microsieverts_per_hour (231)
miles_per_hour (78)
milliamperes (2)
millibars (134)
milligrams(196)
kilograms (39)
milligrams_per_cubic_meter (218)
milligrams_per_gram (211)
milligrams_per_kilogram (212)
milligrams_per_liter (215)
milligray (226)
milliliters (197)
milliliters_per_second (198)
millimeters_of_mercury (59)
millimeters_of_water (206)
millimeters_per_minute (162)
millimeters_per_second (161)
milliohms (145)
milliseconds (159)
millisiemens (202)
millisieverts (229)
millivolts (124)
milliwatts (132)
minutes (72)
minutes_per_degree_kelvin (236)
months (68)
nanograms_per_cubic_meter (220)
nephelometric_turbidity_unit (233)
newton (153)
newton_meters (160)
newton_seconds (187)
newtons_per_meter (188)
no_units (95)
ohm_meters (172)
ohms (4)
parts_per_billion (97)
parts_per_million (96)
pascals (53)
per_mille (207)
per_minute (100)
per_second (101)
percent (98)
percent_obscuration_per_foot (143)
percent_obscuration_per_meter (144)
percent_per_second (99)
pH (234)
pounds_force_per_square_inch (56)
pounds_mass_per_hour (46)
pounds_mass_per_minute (45)
pounds_mass_per_second (119)
power_factor (15)
psi_per_degree_Fahrenheit (102)
radians (103)
radians_per_second (184)
revolutions_per_minute (104)
seconds (73)
siemens (173)
siemens_per_meter (174)
sieverts (228)
square_centimeters (116)
square_feet (1)
square_inches (115)
square_meters (0)
square_meters_per_Newton (185)
teslas (175)
therms (21)
ton_hours (22)
tons (41)
grams_per_minute (155)
tons_per_hour (156)
tons_refrigeration (52)
us_gallons (83)
us_gallons_per_hour (192)
us_gallons_per_minute (89)
volt_amperes (8)
volt_amperes_reactive (11)
volts (5)
volts_per_degree_Kelvin (176)
volts_per_meter (177)
watt_hours (18)
watt_hours_reactive (203)
watts (47)
watts_per_meter_per_degree_Kelvin (189)
watts_per_square_meter (35)
luxes (37)
watts_per_square_meter_degree_kelvin (141)
webers (178)
weeks (69)
years (67)

## Conversions
Idx | Description | Type | Param 1 | Param 2 | Param 3 | Param 4
0 | Limit to 0-100 | FILTER | 2 | 4 | 0 | 100
1 | Limit to 0-255 | FILTER | 2 | 4 | 0 | 255
2 | Is not 0 | FILTER | 0 | 1 | 0 | 100
3 | Is higher than 100 | FILTER | 0 | 3 | 100 | 100
4 | Only positive values | FILTER | 2 | 3 | 0 | 100
0 | Celsius to Fahrenheit | ARITH | -1 | 18 | 32 | 0
1 | Fahrenheit to Celsius | ARITH | -3 | 555 | -17.78 | 0
2 | x10 | ARITH | 1 | 1 | 0 | 0
3 | /10 | ARITH | -1 | 1 | 0 | 0
4 | x100 | ARITH | 2 | 1 | 0 | 0
5 | /100 | ARITH | -2 | 1 | 0 | 0
6 | x1000 | ARITH | 3 | 1 | 0 | 0
7 | /1000 | ARITH | -3 | 1 | 0 | 0
8 | 0-100 to 0-255 | SCALE | 0 | 100 | 0 | 255
9 | 0-255 to 0-100 | SCALE | 0 | 255 | 0 | 100
10 | 12-bit value to percentage | SCALE | 0 | 4096 | 0 | 100